## Sheet1
BTU Calculations for Chilled water or Boilers
Water Properties Estimation
Temperature (deg R) | Specific Heat (BTU/lbm-degR) | Density (lbm/ft^3) | Temp (deg F) | BTU Calculation
495 | 1.006 | 62.42 | 35.33 | Enter Flow (GPM)
540 | 0.998 | 62.23 | 80.33 | 100
585 | 0.999 | 61.61 | 125.33 | Enter Inlet Temp (deg F)
630 | 1.002 | 60.79 | 170.33 | 120
675 | 1.008 | 59.76 | 215.33 | Enter Outlet Temp (deg F)
720 | 1.017 | 58.55 | 260.33 | 40
Enter Time Period for Totalization (min)
60
Inlet Temp (deg R)
579.67
Outlet Temp (deg R)
499.67
Average Temp (deg R)
539.67
Average Temp (deg F)
80
Calculated Density (lbm/ft^3)
62.1548
Calculated Specific Heat (BTU/lbm-degF)
0.9971
Calculated Mass Flow Rate (lbm/min)
706.5795
|  |  |  | Calculated BTU Rate (BTU/min) | Calculated kW Rate
|  |  |  | 56362.3428 | 990.2091
|  |  |  | Calculated BTUs (BTU) in given time period | Calculated kW-h
|  |  |  | 3381740.5662 | 991.0904
Conversion Factors
kW-h = BTU * 0.0002931
kW = (BTU/min) *0.01756863